## Slide 1: Connection design by Component Based Finite Element Method Lecture 3 Column base

## Slide 2: List of lectures
Beam to column moment connection
Joint of hollow to open section
Column base
Seismically qualified joints

## Slide 3: Aims and objectives
Provide information on column base behaviour
Introduce principles of Component Method (CM) for column base design
Introduce principles of Component Based Finite Element Method (CBFEM) for column base
Provide an online training to students and engineers
Show the process of Validation & Verification
Offer list of references relevant to the topic

## Slide 4: Lecture 3 Column base
František Wald, Marta Kuříková, Martin Vild
Lubomír Šabatka, Jaromír Kabeláč, Drahoš Kojala

## Slide 5: Tutorial
This lecture describes principles of Finite Element Method of column base by applying the Component Based FEM (CBFEM).
On the analytical design by Component Method is shown the behaviour of base plate exposed to compression and bending
Validation, Verification and Benchmark cases using Component based Finite Element Method are presented.
Material was prepared under the R&D project MERLION II supported by Technology Agency of the Czech Republic, project No TH02020301.

## Slide 6: Outline of the lecture
Introduction
  Anchor bolts
  Classification
  Assessment I
Component method
  Component in compression
  Component in tension
  Assembly of components
  Assessment II
Component Based Finite Eelement Method
  Validation
  Verification
  Sensitivity study
  Benchmark case
  Assessment III
Summary

## Slide 7: Introduction
Lecture 3
Column base

## Slide 8: Introduction
Steel structures are fixing to concrete foundation/structure by base plate/end plates, embedding and its combination.
The aim of this lecture are joints with base plate fixed to concrete structure by anchor bolts.

## Slide 9: Introduction
The same principles are used for end plate fixed to concrete structure by anchor bolts.
The base plate is usually positioned on the concrete block by pickings or levelling nuts and fixed by grout. The erection has no substantial influence
to design resistance.
If the anchor bolts
are designed
not embedded
(during erection or use)
it takes into account
in design.

## Slide 10: Design resistance of anchor bolt in tension
  Anchor bolts are designed for its resistance in tension according to EN1992-4:2018 for all possible failure modes.
  Basic failure modes in tension are:
    Steel failure of fastener
    Concrete cone failure
    Pull-out failure of fastener
    Note: In structural steel column bases is asked the ductile steel fastener´s failure mode, if structurally possible, compared to anchoring of secondary structures.

## Slide 11: Distribution of forces between anchor bolts in tension
  EN1992-4:2018 expects, that forces between anchor bolts are distributed elastically. It meets the column base with one anchor bolt row.
  Plastic analyses according to CEN/TR 17081:2018 is used for distribution of bolt forces for more anchor bolt rows in tension. In this case is asked to be the govern failure ductile, e.g. the steel failure of fastener. The developed prying forces are taken into account .

## Slide 12: Design resistance of anchor bolt in shear
Anchor bolts for resistance in shear are designed according to EN1992-4:2018 for all possible failure modes.
Basic failure modes in shear are:
    Steel failure of fastener
    Concrete edge failure/Pry-out failure
    Pull-out failure of fastener

## Slide 13: Column base classification
  To simplify global analyses are classified joints in Ch. 5 of EN1993-1-8:2006 based on
  Best engineering practice
  Actual influence of particular joint to current frame design, which implicates recalculation.
  Simplified assumption of frame behaviour
According to initial joint bending stiffness are column bases classified
  Similar to beam-to-column joints
  Related to the column bending stiffness

## Slide 14: Column base classification by bending stiffness
Limit between rigid and semi-rigid column bases based on simplified assumption of frame behaviour.
For non-sway frames is derived from column resistance
for  0,5 Sj,ini  0
for 0,5 < < 3,93 Sj,ini  7 (2 - 1) E Ic / Lc
and for  3,93 Sj,ini  48 E Ic / Lc
where is relative slenderness for simple supported column at both ends.
Is valid for limited stiffness 12 E Ic / Lc
For sway frames is derived from limiting sway
The limit between pinned and semi-rigid is expected 0,5.

## Slide 15: Column base classification by bending stiffness
Below are shown the limits between rigid, semi-rigid column and pinned column bases based on simplified assumption of frame behaviour.
The limits assure accuracy in design of frame 5% for resistance and 20% for serviceability.

## Slide 16
Classification of column base
in non-sway frame
Below is shown the influence of bending stiffness of two column bases to the column buckling length on example of column HEB200.
On the vertical axes is parameter of buckling length β; β = 0,7 for rigid column base and β = 1,0 for pin one. On the horizontal axes is the relative slenderness of base plate to column in logarithmic scale. The points represent influence of the real column bases on buckling length.

## Slide 17
Classification of column base
in sway frame
Below is shown the influence of bending stiffness of column bases in sway portal frame.
On the vertical axes is parameter of sway ys/yp; ys/yp = 0,33 for rigid column base and ys/yp = 1,0 for pin one. On the horizontal axes is the relative slenderness of base plate to column in logarithmic scale. The points represent influence of the real column bases on buckling length of columns.

## Slide 18: Assessment I
What are the basic failure modes of anchor bolts in tension?
What should be the failure mode of anchor bolt in case of plastic distribution of forces in column base with more bolt rows?
What are the basic failure modes of anchor bolts in shear?
What is the reason of classification of joints by bending stiffness?
What principles are used for classification of joints by bending stiffness?
For what accuracy was derived the limit between rigid and semi-rigid column bases for simplified assumption of frame behaviour?

## Slide 19: Component method
Lecture 3
Column base

## Slide 20: Component method for column bases
In the first step of component method is the joint divided into components.

## Slide 21: Component base plate in bending and concrete block in compression
  Base plate is flexible under rigid flange/web plates
  and is taken into account in design by
  Effective rigid area under the flexible plate Aeff.
  Concrete block occurs in spatial stress
  and is taken into account in design by
  Concrete design strength in joint fjd.

## Slide 22: Concrete design strength in joint fjd
  Concrete design strength in joint fjd is derived from the concrete resistance to concentrated force FRd,u.
  where
  j is joint coefficient due to
  lower quality of grout
  compared to concrete
  and is taken 2/3
  fcd is concrete
  compressive strength

## Slide 23: Concrete resistance to concentrated force FRd,u
  Concrete resistance to concentrated force FRd,u is taken as homogenous force FRd,u on the loaded area Ac0. It is limited by geometry of concrete block.
  Note:
  In spatial stress
  is failure mode crushing of concrete under the base plate.

## Slide 24: Concrete resistance to concentrated force FRd,u
  Concrete resistance to concentrated force FRd,u is calculated from geometry of concrete block as
    Ac0 = b1 d1
    Ac1 = b2 d2
    h  b2 – b1; h  d2 – d1
    3  b1  b2 and 3  d1  d2
  where
  fcd is concrete compressive strength
  Ac0 is area of crushing of the concrete
  Cl. 6.7(2) in EN 1992-1-1

## Slide 25: Effective flexible plate on the concrete block
Effective flexible plate on the concrete block, where is reached the concrete design strength in joint fjd, is limited by elastic deformation of the base plate.
From this assumption is calculated effective width c round the column´s flanges/webs as
where
t is the plate thickness
fy is the base plate yield strength
fjd is the design bearing strength of the joint
M0 is the partial safety factor for concrete

## Slide 26
Effective area under the base plate
The effective area of design contact under the base plate is created around the column´s web and flanges by the T-stub effective width c
Into account is taken only real the projection of the physical length of the basic joint component represented by the T-stub.

## Slide 27: Stiffness of component concrete in compression and base plate in bending
Stiffness coefficient of concrete in compression under base plate is taken as deformation of elastic hemisphere
where aeq,el is effective width of T-stub
L is the flange/web length
Effective T-stub width aeq,el in elastic stage may be assumed as

## Slide 28
Comparison to experiments
On the graph is compared the prediction of stiffness of component concrete in compression and base plate in bending.
On the vertical axes is the applied force and on horizontal axes the deformation.

## Slide 29
Influence of grout to column base resistance
Grout with higher strength than concrete block may be taken into account to improve resistance.
Grout with lower strength than concrete block behaves under base plate as liquid and is taken into account by joint reduction factor βj.

## Slide 30: Component anchor bolts in tension and base plate in bending
T-stub created by the base plate, column flange/web and anchor bolts behaves differently compared to the T-stub created by end plate, beam flange/web and bolts in the bolted end plate connection because
  Base plate is thicker
  Anchor bolt free length is longer

## Slide 31: When the prying force may not develop?
The base plate contact to concrete block depends on ration between bolt tensile stiffness and base plate bending stiffness.
Prying forces may develop if
where
Lb is the anchor bolt elongation length, taken equal to the grip length (total thickness of material and washers), plus half the sum of the height of the anchor bolt head and the height of the nut, or the anchor bolt length, taken equal to the sum of 8 times the nominal anchor bolt diameter, the grout layer, the plate thickness, the washer and half the height of the nut,
As is the tensile stress area of the anchor bolt
t is the base palte thickness
Leff is the T stub effective lenght

## Slide 32: Failure mode 1-2 without prying
The failure mode 1-2 is derived to avoid contact of the base plate to the concrete surface.
Design resistance for failure mode 1–2 is governed by plate failure
where m is the lever arm of the anchor bolt.
is the plastic moment resistance of the base plate
with
ℓeff is the effective length of the T-stub and
teff is the base plate thickness.

## Slide 33: Graphical representation of the failure mode 1-2 of the T-stub of anchor bolts in tension and base plate in bending
The difference between failure mode 1 and 2 and failure mode 1-2 is shown on the diagram below, where on vertical axes is acting force F divided by the anchor bolts resistance and on horizontal axes is T-stub bending resistance of base plate divided by the anchor bolts resistance.
Bt.Rd is anchor bolt tensile resistance mpl,Rd is base plate bending resistance of unique length
Failure mode 1

## Slide 34
Anchor bolt effective length Leff
Anchor bolt effective length Leff consists of bolt free length Lbf and free embedded length Lbe .
Leff = Lbf + Lbe
Leff ≈ 8 d
where d is anchor bolt diameter.

## Slide 35: Effective length of T-stub is different in case of prying/no prying
E.g. for base plate with bolts inside the flanges is the effective length
  in prying case
  in no prying case

## Slide 36: Stiffness is different in case of no prying
The stiffness coefficient for plate without prying
is derived the stiffness coefficient for plate as
and for anchor bolt as
where t is the base plate thickness

## Slide 37: Comparison to experiments
The model of anchor bolt in tension is validated against the experiment in Figure below and the good prediction of the resistance and stiffness of the current models is shown.

## Slide 38: Comparison to experiments
The model of the T-stub of component anchor bolt in tension and base plate in bending is validated against the experiment in Figures below and the good prediction of the resistance and stiffness of the current component model is shown.

## Slide 39: Bending resistance
The calculation of the column base resistance is based on the plastic equilibrium of forces on the cross section created by anchor bolts in tension and part of the concrete under base plate in compression.
Then, the column base
moment resistance MRd is

## Slide 40
Interaction diagram
Moment – normal force interaction diagram describes the design resistance of base plate by changing the eccentricity of loading with significant point at changes of effective area.

## Slide 41: Bending stiffness
The column base bending stiffness is derived on simplified model with acting compression force under column flange and tension force in centre of bolt row from the component deformation for two cases
Bolts are activated
Bolts are not activated

## Slide 42: History of loading
The column base bending stiffness depends on history of loading. It is higher, if the column base is first loaded by compression and then by bending compared to, if it is loaded by reverse.

## Slide 43
Comparison to experiment
On Figures below is validated the model of the column base against the experiment to show the good prediction of the resistance and stiffness of the current component model.

## Slide 44: Comparison to experiment
On Figure below is validated the model of the column base proportionally loaded by moment and normal force with the bolt steel failure mode against the experiment to show the good prediction of the resistance and stiffness of the current component model.

## Slide 45: Comparison to experiment
On Figure below is validated the model of the column base non-proportionally loaded by moment and normal force with the concrete cone failure mode against the experiment to show the good prediction of the resistance and stiffness of the current component model.

## Slide 46
Sensitivity study
Figure below shows the sensitivity of the bending moment resistance and the bending stiffness of the column base proportionally loaded by normal force with eccentricity. From base plate thickness are governing anchor bolts.

## Slide 47: Assessment II
What are the basic components on base plate?
What are the major question in design of component in compression?
What is the reason for introducing the joint coefficient?
What is the reason of limiting the effective width of the base plate?
What is the reason, that prying may in case of Failure mode 1-2 not develop?
How is simplified the model of acting compression force for prediction of the column base stiffness?

## Slide 48: Component Based FEM
Lecture 3
Column base

## Slide 49: Concept of Component Based Finite Element Method for column bases
Steel part of column base, column base, column, base plate and stiffeners are simulated by shell models. Resistance is limited by 5% of plastic strain.
Concrete block is taken as component with elastic-plastic surface.
Anchor bolts/welds are modelled as components.
Stress in concrete
Plastic strain in column

## Slide 50: Component concrete in compression
For resistance is considered the part of the concrete block under effective area Aeff only using overlap c, where the base plate deforms in its elastic stage, following the engineering assumption formulated in EN1993-1-8:2006.

## Slide 51: Component anchor bolt in tension
The resistance of the anchor bolt in tension is taken from concrete components resistance and from the steel one.
Maximum allowed plastic strain for anchor bolts εmpb is taken as 25 % of elongation till fracture.
The stiffness in tension is calculated as k = E As/Lb, where As is tensile area of anchor bolt and Lb is the distance between the centers of the head and the bolt nut.
Vertical force in anchor bolt, kN
Vertical deformation, mm
uel
ut,Rd
Ft,Rd
Ft,el
Fc,Ed
k
kt

## Slide 52: Component anchor bolt in shear
The resistance of anchor bolt in shear is calculated according to EN1992-4:2018 and EN1993-1-8:2006.
Stiffness of anchor bolt in shear includes bearing of concrete and bending of bolt.
Shear force in anchor bolt, kN
Horizontal deformation, mm
uel
ut,Rd
Ft,Rd
Ft,el
Fc,Ed
k
kt

## Slide 53: Normal force and bending moment interaction diagram
The cross section under base plate consists of anchor bolts and contact to concrete.
The significant points on interaction diagram reflects changes of geometry of compressed part.
The cross section exposed to normal force and bending behaves like concrete column cross section of effective contact area.
Chart: Normal force NRd [kN]
| 113.44313578797671 | 0 | -764.92281303860534 | -969.27320390628881 | -1173.6235947739724 | -2124.8452463621661
ŠROUBY MIMO PRŮŘEZ | 0 | 35.3605 | 139.189 | 158.9348 | 139.189 | 0
Point -1
Point 0
Point 1
Point 2
Point 3
Point 4

## Slide 54: Experiments for validation
For validation were prepared two experiments in uniaxial and two in biaxial bending at TU Brno.
The experimental set ups is presented below.
Uniaxial bending
Biaxial bending

## Slide 55: Experiment´s general data
Column HEB 240
Concrete block 1000x1200x9000 C20/25
Base plate 330x440x20 S235
Anchor bolts 4 x M20
Grout 30 mm
Bending of set up in biaxial bending

## Slide 56: Behaviour of base plate in case of uniaxial bending
Set up in uniaxial bending
Deformed base plate

## Slide 57: FE prediction of column base behaviour in uniaxial bending
Figure below shows the equivalent stresses in base plate and in concrete calculated by CBFEM.

## Slide 58: Validation of models to experiments in uniaxial bending
Chart: Rotation 𝜙 [mrad]
| 0 | 1.100775153684354 | 1.1666857021767374 | 1.2354305424440377 | 1.3070852182776371 | 1.3817260898376944 | 1.4594303299293649 | 1.5402759203515428 | 1.6243416483156401 | 1.7117071029320723 | 1.8024526717622182 | 1.8966595374337214 | 1.9944096743170996 | 2.0957858452617413 | 2.2008715983894103 | 2.3097512639435194 | 2.422509951192453 | 2.5392335453853359 | 2.6600087047586944 | 2.78492285759252 | 2.9140641993143039 | 3.0475216896497055 | 3.1853850498184939 | 3.3277447597745606 | 3.4746920554887457 | 3.6263189262733451 | 3.7827181121471658 | 3.9439831012400624 | 4.1102081272359205 | 4.2814881668530784 | 4.4579189373612538 | 4.6395968941340131 | 4.8266192282359262 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097 | 4.9344218685755097
CM | 0 | 63.1273 | 64.1273 | 65.1273 | 66.1273 | 67.1273 | 68.1273 | 69.1273 | 70.1273 | 71.1273 | 72.1273 | 73.1273 | 74.1273 | 75.1273 | 76.1273 | 77.1273 | 78.1273 | 79.1273 | 80.1273 | 81.1273 | 82.1273 | 83.1273 | 84.1273 | 85.1273 | 86.1273 | 87.1273 | 88.1273 | 89.1273 | 90.1273 | 91.1273 | 92.1273 | 93.1273 | 94.1273 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909 | 94.6909
CBFEM | 0 | 10 | 20 | 30 | 60 | 80 | 90 | 100 | 110 | 120 | 125 | 130 | 135 | 140
Figure left shows on moment rotation diagram a good prediction capacity of resistance of both Component (CM) and Component Based FE model (CBFEM).
CBFEM compared to CM predicts higher resistance. It includes real space stress in concrete.
The bending stiffness of experiments is lower compared to prediction.
The predictive model shows compared to experiments the safety due to conservative proposal of anchor bolt.
Notes: Design model – design values of yield strength etc.
Concrete failures not taken into account

## Slide 59: Validation of CBFE model to experiment in uniaxial bending
Chart: Bending moment My [kNm]
| 0 | 10 | 20 | 30 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 125 | 130 | 135 | 140
B3+B4 | 0 | 0 | 0 | 0 | 14.7 | 28.3 | 42.8 | 57.9 | 73.2 | 88.8 | 99.9 | 111.4 | 121.6 | 138.05
Figure left shows on anchor force – bending moment diagram a good prediction capacity of Component Based Finite Element Model.
The predicted bolt force is conservatively higher compared to measured ones on both experiments.
Notes: Seems that base plate yields later and the anchors are less stiff in reality

## Slide 60: FEA model for column base in biaxial bending
Figure below shows the equivalent stresses in base plate and in concrete in Component Based FE model

## Slide 61: Validation of model to experiments in biaxial bending
Figure left shows on moment rotation diagram a good prediction capacity of resistance of Component Based FE model.
The bending stiffness of experiments is lower compared to prediction.
The predictive model shows compared to experiments the safety due to a conservative proposal of anchor bolt.
Chart: Deformation δh [mm]
| 0 | 1.9417475728155338 | 2.9940119760479043 | 4.2553191489361701 | 5.7208237986270021 | 7.3710073710073702 | 9.1623036649214669 | 11.173184357541899 | 14.240506329113924 | 20.746887966804977 | 29.569892473118276 | 48
CBFEM | 0 | 18.3 | 27.45 | 36.6 | 45.75 | 54.9 | 64.05 | 73.2 | 82.35 | 91.5 | 100.65 | 109.8
Notes: Design model – design values of yield strength etc.
Concrete failures not taken into account

## Slide 62: Validation of CBFE model to experiment in uniaxial bending
Figure left shows on the anchor forces – bending diagram a good prediction capacity of Component Based FE model for the most loaded anchor bolt.
The predicted bolt force is conservatively higher compared to the measured ones.
Chart: Bending moment M [kNm]
| 0 | 18.3 | 27.450000000000003 | 36.6 | 45.75 | 54.900000000000006 | 64.05 | 73.2 | 82.350000000000009 | 91.5 | 100.65 | 109.80000000000001
B3 | 0 | 0 | 4.1 | 14.1 | 27.7 | 43.7 | 61.5 | 81.2 | 97 | 102.8 | 109.8 | 123.7
B4 | 0 | 0 | 0 | 0 | 0 | 3.2 | 8.1 | 13.9 | 26 | 56.3 | 90.4 | 99.2
Notes: Seems that base plate yields later and the anchors are less stiff in reality

## Slide 63: Verification column base for SHS 160
In following example, the column from square hollow section SHS 150x16 is connected to concrete block with the area dimensions , and height from concrete grade C20/25 by the base plate ; ; from steel S420. Anchor bolts are designed 4 x M20, As = 245 mm2 with head diameter a = 60 mm from steel 8.8 with offset at top 50 mm and left -20 mm. Grout has the thickness of 30 mm.

## Slide 64: Bending moment - normal force interaction diagram
Chart: Normal force [kN]
| 79.965353854514049 | 0 | -756.1184320341489 | -912.95767479490235 | -1069.7969175556561 | -1947.462687448666
CM | 0 | 14.2233 | 62.3285 | 64.021 | 62.3285 | 0
CBFEM | 0 | 14 | 55 | 62 | 68 | 0
The resistance of column base predicted by CBFEM is compared to CM on moment – normal force interaction diagram for base plate 10 mm in Figure below.

## Slide 65: Significant points on the bending moment – normal force interaction diagram
Pure tension Pure bending
The equivalent stresses at the edge of the thin base plate (10 mm) loaded in pure tension show the plate contact and possible development of prying forces.

## Slide 66: Significant points on the bending moment – normal force interaction diagram
Flange in compression Half of cross section in compression
The equivalent stresses and the design effective area of the contact of base plate to concrete block.

## Slide 67: Significant points on the bending moment – normal force interaction diagram
Webs in compression Pure compresion
The equivalent stresses and the design effective area of the contact of base plate to concrete block.

## Slide 68: Verification for pure compression
Chart: Component Method [kN]
| 0 | -5000
 | 0 | -5000
 | 0 | -4500
 | 0 | -5500
4 | -1788 | -2317 | -2527 | -1788 | -1950 | -2499 | -1625 | -2860 | -3904 | -2071 | -2219 | -2219 | -2859 | -2868 | -2845
The resistance of column base predicted by CBFEM is compared to resistance predicted by CM in case of pure compression in Figure below.
The graph shows similar prediction capability of both methods.

## Slide 69: Verification for pure bending
Chart: Component Method [kNm]
| 0 | 1000
100% | 0 | 1000
90% | 0 | 900
110% | 0 | 1100
0 | 14 | 17 | 18 | 14 | 14 | 18 | 13 | 19 | 20 | 9 | 24 | 44 | 19 | 23 | 27
The resistance of column base predicted by CBFEM is compared to resistance predicted by CM in case of pure bending in Figure below.
The graph shows similar prediction capability of both methods. CBFEM predicts a bit higher resistance due to taking into account prying forces.

## Slide 70: Sensitivity study base plate thickness; 10; 20; 30 mm
Chart: Normal force, NRd [kN]
| 99.666666666666742 | 0 | -506.42463146272064 | -839.16927952907963 | -1171.9139275954383 | -1820.3635590581594
An_10 | 0 | 18.7254 | 63.7761 | 74.9674 | 63.7761 | 0
An_20 | 0 | 19.9695 | 111.1575 | 120.3265 | 110.0476 | 0
An_30 | 0 | 21.311 | 165.4879 | 178.6463 | 173.8253 | 0
IC_10 | 0 | 13 | 51 | 71 | 68 | 0
IC_20 | 0 | 19 | 95 | 119 | 133 | 0
IC_30 | 0 | 20 | 132 | 153 | 158 | 0
CM
CBFEM
The resistance of column base predicted by CBFEM is compared to CM on moment – normal force interaction diagram for base plates 10 mm, 20 and 30 mm in Figure below.

## Slide 71: Open section column loaded in compression
Inputs
  Column, cross section HEB 240, steel S235
  Base plate, thickness 20 mm, offsets top 100 mm, left 45 mm, steel S235
  Concrete block, concrete C20/25, offset 335 mm, depth 800 mm, grout thickness 30 mm, grout quality C20/25
  Anchor bolt, M20 8.8
Output
  Axial force resistance Fj.Rd = -1744,2 kN

## Slide 72: Hollow section column loaded in compression and bending
Inputs
  Column cross section: SHS 150/16, steel S460
  Base plate: thickness 20 mm, offsets at top 100 mm, on left 100 mm, welds 8 mm, steel S460
  Anchor bolts: M20 8.8., anchoring length 400 mm, offsets top layers 50 mm, left layers -20 mm, shear plane in thread
  Foundation block: concrete C20/25, offset 200 mm, depth 800 mm, shear force transferred by friction
  Grout thickness 30 mm
  Loading
    Axial force N = -913 kN
    Bending moment My = 62,1 kNm

## Slide 73: Hollow section column loaded in compression and bending
Outputs
  Plate ;
  Anchor bolts 99,7 % ( (critical component concrete cone breakout)
  Welds 57,7 % ()
  Concrete block 83,0 % ()
  Secant rotational stiffness

## Slide 74: Assessment III
How is limited in CBFEM the resistance of base plate?
How is modelled in CBFEM for column base design the concrete block?
Which part under base plate is considered in roe resistance?
How is limited the design of anchor bolts?
What is difference between design of column base and concrete column in compression?
What is the reason for higher resistance of column base in tension with base plate in failure mode 1-2?

## Slide 75: Summary
Lecture 3
Column base

## Slide 76: Summary
The column bases are designed with plastic distribution of forces under base plate.
Concrete in compression under the base plate is designed taking into account its spatial stress.
The homogenous stress under the flexible base plate is expected for elastically deformed base plate.
Column bases are often exposed to interaction of normal force and bending moments.

## Slide 77: Summary
If more anchor bolts rows are activated, only the steel failure of anchor bolt is allowed to ensure the ductile failure.
In Component Method limits the prying of anchor bolts failure mode 1-2.
In CBFEM are taken into account prying forces. if it decides on the bearing capacity and the anchoring to concrete is strong enough, the predicted resistance may be higher.

## Slide 78: What is the major reason for using CBFEM for column bases?
Resistance limited by anchor bolt failure
  Strain 3,4 %
  Prying forces are taken into account
Foot print Stress
Generally loaded complex column base is very difficult to design by Component Method.
The example of design by CBFEM is shown below.
Strain

## Slide 79: Thank your for attention
URL: steel.fsv.cvut.cz
František Wald, Martin Vild, Marta Kuříková,
Luboš Šabatka, Jaromír Kabeláč, Drahoš Kojala

## Slide 80: Notes to users of the lecture
Subject Design of column bases of steel structures.
Lecture duration 60 mins
Keywords Civil Engineering, Structural design, Steel structure, Column base, Steel to concrete connection, Joint, Component Method, Component based Finite Element Method, Anchor bolts, Eurocode.
Aspects to be discussed Design of anchor bolts, Reasons and methods of classification, Principles of CM, Components in column base for CM, Components in column base for CBFEM, Principles of CBFEM, Spatial stresses in concrete block, Model of stress distribution under the base plate.
Further reading relevant documents in references and relevant European design standards, Eurocodes including National Annexes.
Preparation for tutorial exercise see examples in References.

## Slide 81: Sources
Bajer M., Vild M., Barnat J., Holomek J., Influence of Selected Parameters on Design Optimisation of Anchor Joint, in Steel, Space and Composite Structures, Singapore, 2014,149–158.
Kuhlman U., Krimpmann M., Hofmann J., Wald F., et al, Design of steel-to-concrete joints, Design manual II, ECCS Brussels, 2013.
Steenhuis M., Wald F., Sokol Z., Stark J.W.B., Concrete in Compression and Base Plate in Bending, Heron, 2008, 53, 1/2, 51-68.
Wald F. et al, Benchmark cases for advanced design of structural steel connections, Česká technika ČVUT, 2016.
Wald F., Gödrich L., Šabatka L., Kabeláč J., Navrátil J., Component Based Finite Element Model of Structural Connections, in Steel, Space and Composite Structures, Singapore, 2014, 337-344.
Wald F., Sokol Z., Steenhuis M., Jaspart, J.P., Component Method for Steel Column Bases, Heron, 53, 2008, 3-20.
Wald F., Sokol, Z., Jaspart J.P., Base Plate in Bending and Anchor Bolts in Tension, Heron, 2008, 53, 1/2, 21-50.

## Slide 82: Standards
CEN/TR 17081:2018 Design of fastenings for use in concrete - Plastic design of fastenings with headed and post-installed fasteners, CEN, Brussels, 2018, ready for release.
EN1992-1-1:2006, Eurocode 2, Design of concrete structures, Part 1-1, General rules and rules for buildings, CEN, Brussels, 2006.
EN1992-4:2018 Eurocode 2, Design of concrete structures – Part 4: Design of fastenings for use in concrete , CEN, Brussels, 2018, ready for release.
EN1993-1-8:2006, Eurocode 3, Design of steel structures, Part 1-8, Design of joints, CEN, Brussels, 2006.
EN1994-1-1:2010, Eurocode 4, Design of composite steel and concrete structures, Part 1-1, General rules and rules for buildings, CEN, 2010.
ETAG 001: 2010, Guideline for European Technical Approval of Metal Anchors for Use in Concrete – Annex C: Design Methods for Anchorages, Brussels, EOTA, 2010.

## Slide 83: The standards related to anchor bolts
Till the end of last century were anchor bolts designed according to experimental results summarised in design tables.
Majority or current standards for anchorages to concrete are based on failure mode method, Concrete capacity design method, developed by prof. R. Eligehausen and his students at University of Stuttgart, see Eligehausen R., Mallée R., Silva J. F., Anchorage in concrete construction, Ernst & Sohn, 2006.
Currently is used in Europe for design Annex C in ETAG 001:2010 Metal anchors for use in concrete, https://www.eota.eu/en-GB/content/etags-used-as-ead/26/.
Prestandard prEN 1992-4 was published in 2010 and valid for three years. In 2018 is expected to be published EN 1992-4:2018, which will replace Annex C in ETAG 001.
American and Canadian standards are nearly identical. American standard ACI 318 used to contain anchorage design in Annex D. In the version from the year 2014 is described in Ch.17. Canadian standard A23.3 contains anchorage design in Annex D.
Australian standard SA TS 101:2015 is fully compatible with ETAG, http://www.aefac.org.au.